### TO BE ADDED TO THE GENERAL NOTES

FOR ALL

STREET LIGHT IMPROVEMENT PLANS

- All roadway lighting, except as indicated hereon, shall be done in strict conformance with the current City of Ontario Standard Specifications and Standard Drawings.

- All cables, wires and conductors shall be delivered new to the site and shall be pulled continuously from light standard to feed point.  Splicing is allowed in pull boxes only.  Splicing is not allowed in conduits or street light standards.  Conductors shall be spliced by the use of compression connectors and insulation shall be by “Method B,” as shown on Caltrans Standard Plan, ES-13.  Wire nuts are not allowed.

- Wiring shall be Poly Vinyl-Chloride Insulated (Type THW, or THNN) 600V – NO. 8 AWG Copper Cable per the standard specifications or approved equal. Number 12 AWG copper cable shall be allowed in the light standards.

- All conduits shall be 1 ½” rigid metallic or Schedule 80 PVC. Unless otherwise noted.  Conductors shall conform to the following colors: Conductors for grounding and bonding shall be bare or green, common or neutral conductors shall be white, underground-line 1 conductors shall be black, underground-line 2 conductors shall be red.

- A number 3 ½ pull box shall be installed 6” behind curb in line with the center of the light standard on side nearest the flow of oncoming traffic.  The pull box shall be sloped at ¼” per foot to top of curb, fitted with a fused splice connector conforming to Caltrans Standard Specification, Section 86-2.095.  The fuse connector shall be Bussman – Type TRON-HEB for 120v, or TRON-HEX for 240v, with Type KTK fuses rated at 20 amps (Bussman Bulletin SPF-11).  Refer to City of Ontario Standard Drawing Street Light Installation Detail.

- All new luminaire circuits shall operate on 240 volts, and bonding of circuits shall be per applicable codes.  The contractor shall verify the voltage of the existing luminaries.

- Poles shall be from one manufacturer and shall be mounted in center of foundation per Ontario Standard Drawing Street Light Standard.

- All foundations shall be adjacent to back of curb, and all anchor bolts shall be 1” X 36” X 4”, and project 4 ½” above top of foundation.  Cap with 5” of grout sloped at ¼” per foot to top of curb.  Refer to Ontario Standard Drawing Street Light Standard and Installation Detail.

- The contractor shall supply and install all materials including photoelectric control circuit-breakers and auxiliary relay(s).  Southern California Edison will furnish and install service conductors to the landing lugs per City of Ontario Standard Drawings Underground Electrical Feed Point and Street Light Pedestal Wiring Diagram.  All work related to electric service shall be performed in conformance with the requirements of the Southern California Edison Company.

- Circuit protection shall be provided as follows: 15 amp for photoelectric control, 30 amp single or double pole for each circuit as required.  A shorting cap shall be installed in the photoelectric control receptacle of all light standards.  A 5/8” X 8’ Blackburn copper clad ground rod, or equivalent, with copper weld ground clamp, or equivalent, shall be installed in the underground electrical feed point (service pedestal).  Refer to Ontario Standard Drawing Underground Electrical Feed Point.

- State law CAL/OSHA Electrical Safety Order 2946 requires a minimum clearance of 10 feet from overhead high voltage lines and street lights and operating boom-type lifting or hoisting equipment.

- At the direction of the Engineer, the contractor shall deliver and unload any salvage to the Ontario Municipal Service Center, 1425 South Bon View Avenue, or City well site no. 9 on the west side of Columbia Avenue north of Deodar Street or south of Ontario Municipal Service Center Cucamonga Avenue driveway.

- Contractor shall be responsible to determine and field verify existing electrical service feed point locations for project proposed and existing street lights and provide locations on record drawing markup.

- Contractor shall refer to the project specifications and the City of Ontario Approved Material List (AML) LED Luminaires for acceptable manufacturers and required LED lamp group model numbers.

- Contractor shall be responsible to field verify that the proposed street light pole installation locations will meet the required California Public Utilities Commission minimum radial clearances for existing overhead utility lines prior to submitting material cutsheets for approval and ordering material.